## Sheet1
FAO: EVC
cc: COO, CTO, ED (O&SD), ED (F&SD)
DAILY OPERATIONAL REPORT FOR 13 AUGUST 2026
A: GENERATION
UNITS | PRESENT DAY RECORDS |  |  | PREVIOUS DAY RECORDS | [6 empty] | COMMENTS
| AVAILABLE CAPACITY (MW) | DECLARED CAPACITY (MW) | LOAD AT 06.00HRS (MW) | DECLARED CAPACITY (MW) | DECLARED HOURS | TOTAL HOURS RUN | DERATED HOURS | EXPECTED GENERATION (MWh) | ACTUAL GENERATION (MWh) | ENERGY DEFICIT (DERATED GENERATION) (MWh) |  |  |  |  | 0
411G1 | 150 | 150 | 149.35 | 150 | 24 | 24 | 0 | 3600 | 3278.7 | 321.3 | Unit operated overnight on loads ranging from 141.62MW to 149.35MW on free governor response. Unit is currently loaded to 146.01MW still on free governor response (50.25Hz at 08.00hrs of 13/08/26).
411G2 | 150 | 150 | 145.79 | 150 | 24 | 24 | 0 | 3600 | 3348.6 | 251.4 | Unit operated overnight on loads ranging from 126.89MW to 145.79MW on free governor response. Unit is currently loaded to 142.07MW still on free governor response (50.25Hz at 08.00hrs of 13/08/26).
411G3 | 150 | 150 | 147.03 | 150 | 24 | 24 | 0 | 3600 | 3237.4 | 362.6 | Unit operated overnight on loads ranging from 135.37MW to 146.54MW on free governor response. Unit is currently loaded to 135.87MW still on free governor response (50.25Hz at 08.00hrs of 13/08/26).
411G4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Francoray Dive and Marine Services Limited has carried out a comprehensive inspection of Unit 411G4 Penstock from 25/01/24 to 15/03/24. A formal report on the inspection project has been produced, and discussed on Wednesday 24/04/24. TRACTEBEL ENGINEERING Consultants were on site from Wednesday 29/05/24 to Thursday 30/05/24 to assess requirements and provide Engineering Services for restoration of the penstock. Inspections were carried out from both the scroll case and power intake ends of the penstock. Preliminary reports have been submitted. Tractebel is now developing a technical soluton for restoration of unit 411G4 penstock.
TOTAL | 450 | 450 | 442.17 | 450 |  |  | 2 | 10800 | 9864.7 | 935.3
Station Service Consumption (MWh) |  |  | 38.6 | Energy Sent Out (MWh) |  |  |  | 9826.1 | Maximum Load Generated (MW) |  | 450.86 | @ | 06.00hrs
Average Generation for the Day (MW) |  |  | 411.0292 | Declared Capacity Utilization (%) |  |  |  | 91.3398 | Plant Water to Power Ratio |  | 1.1536 | Station Water to Power Ratio |  | 1.1536
B: HYDROLOGICAL DATA AS AT 12 AUGUST 2026
ELEVATIONS (m) |  | Head Water |  |  | 367.5 |  | Tail Water | 271 | Gross Operating Head | 96.5
FLOWS (m3/s) |  | Average Computed Inflow |  |  | 1036.67 |  | Average Turbine Discharge | 474.17 | Spillage / Gate Overflow over the past 24 hours | 0 | Average Station Total Discharge over the past 24 hours | 474.17 | Storage Differential | 562.5
STORAGE |  | % Live Volume Available |  |  | 36.3
The two available dewatering pump Nos. 1 and 2 had issues in quick succession when deployed to dewater unit 411G3 draft tube. Pump No. 2 had seal failure on Tuesday 07/01/25 but has been replaced with a refurbished pump and put to use. Pump No. 1 on Wednesday 08/01/25 draws high current in service. Maintenace team has investigated this trend. A test-run will be scheduled after a faulty monorail is replaced with a new one for safe materials handling. Mono-rail has been supplied, installed, tested and commissioned. Work on the unwatering pumps will continue when manpower needs of the overhaul project reduces. Work has resumed and unwatering pumps 2 and 4 are now available.
Unit 411G2 Governor oil pump No. 1 was observed making abnormal noise and was repplaced with another governor oil pump taken from unit 411G4. After installation, this replacement could no respond to both manual and auto schemes. Investigation is continuing. Meanshile, unit 411G2 was returned to service at 18.27hrs of 02/07/26 after the 1800 service hours inspection and maintenance, running on governor oil pump No 2 alone. Further tests will be carried out during the next 1800 service hours inspection and maintenance of the unit (when reservoir draw-down commences in the current year 2026).